## Sawyer
HEATH TOWN BUILDING REPAIRS |  | Red fill indicates committee feels repair is urgent
| Immediate Needs | Current Condition | Within 5 years | Future Needs
Sawyer Hall | Install HC Parking spot with signage | No HC parking or signage
| Repair pavement at bottom of ramp | Caved and unlevel
| Re-level ramp slate, make gaps less than 1/2" | Slate has heaved, creating >1/2" changes in level
| Install handrails on front entrance exterior stair | No handrails
| Replace or modify entry door threshold | Threshold elevation change>1/2"
| Install emergency lighting on all exit discharges | No emergency lighting as prescribed by code
| Install light on exterior stair from 2nd floor | No light
| Re-set concrete, rear stair and platform | Precast unit has heaved and created an elevation change and tripping hazard.
| Extend surface drain pipe at rear exit away from concrete slab. | Drain pipe obstructs exit path
|  | 2nd floor exterior stairway does not discharge to public way | Connect discharge from 2nd floor exterior stair to ramp
|  | Stairs and platform out of level with >7" risers, no lighting | Rear exit to library: Replace exterior landing and stairs. Add lighting
|  | Rear exit to library does not discharge to public way | Connect rear exit discharge to library to street
Building | Immediate Needs | Current Condition | Within 5 years | Future Needs
Sawyer Hall | Replace and paint rotted, exterior trim boards | Some freeze and corner boards, window trim rotted
| Repair slate&ridge cap on rear roof | North side ridge cap and slate shingles missing or damaged
| Basement (mechanical room): Remove files, install back-up pump, check ground-fault outlet for pump that trips with power outage, replace fiberglass insulation with foam. | Flooding occurs when pump fails or power outage. Boiler and electrical service in danger. Stored files collect moisture. | Elevate furnace.
| Main basement: remove junk, repair plastic vapor retarder | Some junk in basement, part of plastic vapor retarder out of place
|  | Persons entering hall from vestibule can be hit by outswinging door | Change windows in vestibule doors to for better visibility
| Remove all files not required for current use & store in new location, if needed. | Cluttered desks, little file organization
Replace lighting with LED lights whereever possible.
| Make Library ADA compliant. | Aisles not at least 36", top and bottom shelving not reachable
| Interior and exterior painting | In need
|  | No security system | Install security system
|  | Oil-fired baseboard heat |  | Install air-source HVAC system.

## Community Hall
HEATH TOWN BUILDING REPAIRS |  | Red fill indicates committee feels repair is urgent
Building | Immediate Needs | Current Condition | Within 5 years | Future Needs
Community Hall
| Replace broken windows. | Some windows broken, creating hazard
| Investigate cause for leak on North wall of kitchen, check for mold. | Water-damaged sheetrock above window
| Repair gutters, install leaf guard. | Gutters pitched improperly(probable cause of kitchen leak), too high to access to clean.
| Replace missing shingles | Some shingles missing on SW end
| Check attic area above balcony for possible water infiltration | Stained ceiling in balcony
|  | Shingles look good, about 20 yrs old | Re-roof ashalt shingles
|  | Painting not too bad | Paint exterior
| Install new storm windows. | Single pane windows
| Improve drainage outside Senior Center entrance to avoid icing. | Parking area for lower halls experiences icing in winter
| Install interior handles on windows, rework pulleys and weights | Lack of handles may cause window breakage by users trying to push windows up, original operating system
| Remediate asbestos in furnace room. | Asbestos found, furnace room locked
| Replace swinging entry doors with airtight doors. | Rusty, not airtight
| Insulate walls. | No insulation in walls
| Replace lighting with LED lights wherever possible. | Lights not energy efficient
| Install air-source HVAC system. | Inefficient oil-fired forced air
| Remove all materials currently in balcony & store in new location, if needed. | Space not being used, cluttered
| Repair floor at Senior Center entrance. | Floor near entrance door damaged
| Clear access to elevator in senior center as needed to meet ADA requirements. | Stored items block access

## Highway Garage
HEATH TOWN BUILDING REPAIRS |  | Red fill indicates committee feels repair is urgent
Building | Immediate Needs | Current Condition | Within 5 years | Future Needs
Highway Garage | Insulate walls(less than R-4) | Less than R-4
| Repair siding | holes in siding/walls can see daylight
| Replace side entry door | Rusty, 2"gap at floor
Insulate ceiling(only R-12)
| Replace windows | Single pane, not air-tight
| Replace damaged garage door panels(3) | dented
| Size and add ventilation with heat recovery | Ventilation inadequate and seldom used in winter
| Test water, filter accordingly | Well contaminated, not drinkable
| Provide exhaust ports in doors | None
Add conditioned storage space for tools, oil, compressor, etc.
Provide sufficient office space for superintendent(just barely enough now for a desk)
Provide space for another desk(when plow in garage, cannot access desk or office)
Provide more space(currently 3 bays for 5 trucks) with addition or new building

## Fire Station
HEATH TOWN BUILDING REPAIRS |  | Red fill indicates committee feels repair is urgent
Building | Immediate Needs | Current Condition | Within 5 years | Future Needs
Fire Station | Repair foundation pilasters,cap | Pilasters missing
| Repair concrete blocks | Some blocks crumbling
| Repoint blocking | Missing grout
| Test water, filter accordingly | Well contaminated, not drinkable
| Re-wire | Patched wiring, short-run splices, fuse box
| Replace lighting | Lights are not hard-wired; they have plugs
| Overhead doors tracks and openers need service | At least 2 occassions where doors did not open or close
| Replace oh door panels(2) | Dented
|  | When fire trucks parked, insufficient room to walk. Size of bays limit FD on choice of trucks | Provide longer bays with addition or new building

## EOC
HEATH TOWN BUILDING REPAIRS |  | Red fill indicates committee feels repair is urgent
Building | Immediate Needs | Current Condition | Within 5 years | Future Needs
EOC | Provide accessible entrance | Not accessible
| Insulate floor and walls | No insulation in floor or walls
| Remove misc storage from attic, air-seal, insulate R-38 min | 3 1/2" batt, disturbed because of storage
| Re-wire | Patched wiring, fuse box. Generator does not power room.
| Roof replacement | Original metal roof, leaks
| Test water, filter accordingly | Well contaminated, not drinkable
| Provide clean water for washing, shower, eye wash | Shares single toilet room with contaminated water with highway dept.
| Repair sheet rock | Damaged
| Clear trees, create swale in back of building | Water flows at and under building, damaging block foundation and contributing to mold issue

## Salt Shed
HEATH TOWN BUILDING REPAIRS |  | Red fill indicates committee feels repair is urgent
Building | Immediate Needs | Current Condition | Within 5 years | Future Needs
Salt Shed | Repair broken truss | trusses are 4ft on center--dangerous condition
| Check remainder trusses for damaged plates, bracing, and tie down | Uncertain
| Repair interior walls and bracing | Interior walls not high enough and damaged severely, braces for walls broken
Replace or rebuild

## School
HEATH TOWN BUILDING REPAIRS |  | Red fill indicates committee feels repair is urgent
Building | Immediate Needs | Current Condition | Within 5 years | Future Needs
School | Roof repair in NW corner/valleys | Leaking in cafeteria
| Replace caulk between aluminum window frames and brick masonary | Caulk cracked and missing in places
| Infrared test of main switchgear & distribution | Should be done every 5 years. Has not been done yet.
| Chimney cap on furnace chimney | No chimney cap
| Refinish oak window sills | In need of refinishing
| Insulate ductwork in attic | Some ductwork not insulated
| Insulate copper water piping in attic | Some piping not insulated
| Complete addition of loose cellulose insulation in attic in areas of settlement | Some insulation not done
| Repairs to soffit near loading dock | Slightly damaged
|  | Dents in ceiling, broken light fixture | Repair & repaint entry canopy
|  | Generally ok for now | Paint facia and rake trim
|  | Some cracking | Repair tile flooring
|  | Will not hold temperature |  | Repair or replace refrigerator bank
|  | Cracking and heaving in places | Repair asphalt in driveway/parking area | Repave driveway/parking areas
|  | Cracking and heaving in places | Replace damaged walkways
|  | Except for NW valley, ok |  | Re-roof
|  | Original units(24yrs old) | Replace furnaces